TOWN OF PAXTON

BOARD OF HEALTH

(revised 3.1.2020)

APPLICATION  FOR PRIVATE WATER WELL CONSTRUCTION

FEE:   $100.00___

Application is hereby made for a permit to construct a Private Water Well at:

LOCATION – ADDRESS						LOT NO.

________________________________________________________________________
OWNER				Phone Nos.			 ADDRESS

INSTALLER				Phone Nos.			 ADDRESS

TYPE OF WELL:  ________________________________________

DISTANCE FROM PUBLIC WAY:__________________________

DISTANCE FROM SEWAGE SEPTIC TANK (50’ min.) __________________

DISTANCE FROM SEWAGE DISPOSAL FIELD (100’ min.):______________

DISTANCE FROM PROPERTY LINE (25’ min.):________________________

SHOW ANY SEPTIC SYSTEM WITHIN 200’:__________________________

AGREEMENT:

The undersigned agrees to construct the aforesaid water well in accordance with the

Provisions of the Private Well Regulations promulgated by the Board of Health, Paxton, MA that went into effect January 6, 2004 and further agrees not to utilize the water from said well for human consumption until a Certificate of Compliance has been issued by the Board of Health.

SIGNED: ______________________________ DATE: ______

application approved by: ______________________________ DATE: ______

APPLICATION DISAPPROVED FOR THE FOLLOWING REASONS: ____________
________________________________________________________________________

PERMIT NO.	____________			DATE ISSUED:  _______________

TOWN OF PAXTON BOARD OF HEALTH

PRIVATE WATER WELL REGULATIONS

PART ONE – GENERAL

SECTION  I.  AUTHORITY

The Paxton Board of Health promulgates these regulations pursuant to Mass.

General Laws, Chapter 111, Section 31.  They will become effective on

January 6, 2004.

SECTION II:  REGISTRATION OF WELL DRILLERS

Wells shall be constructed only by registered well drillers licensed by the

Commonwealth of Massachusetts.

SECTION III:  WELL CONSTRUCTION PERMITS

a.	No well construction permit shall be issued where the town public water supply is available and feasible as determined by the Department of Public Works (Water Board or Water Department).

b.	A well construction permit shall be obtained from the Board of Health prior to the construction of a water well.

c.	An application for said permit and a plot plan shall be submitted to the Board of Health by the drilling contractor on the appropriate form.  Said permit shall be obtained prior to any well construction.

d.	In the case of new building construction which will rely on a private well as a source of potable water, a well shall be installed and tested for quality and quantity prior to the issuance of a building permit.

e.	The location, design and operation of the water well must be approved by the Board of Health before being used as potable water supply.

f.	Well test results are valid for one year from the test date.

PART TWO – WELL CONTRUCTION

SECTION I.  LOCATION RELATIVE TO CONTAMINANTS & POLLUTANTS

a.	All wells shall be located at an adequate horizontal distance from potential sources of contamination and pollution.  The following minimum lateral distances shall apply to sources of contamination as listed:

Sources of Contamination                                     Minimum lateral distances

1.  Subsurface disposal fields including 		100 feet

the designated reserve area.

2.  Cesspools, seepage pits				100 feet

3.  Septic Tank, sewer					  50 feet

4.  Property Lines					  25 feet

5.  Public Ways					  25 feet

6.  Open and Subsurface drains			  25 feet

7.  Building or projection thereof			    5 feet

b. Where possible, the well shall be located above the ground-water gradient (upstream)

from sources of contamination.

SECTION II.  CASING.

a.  The casing must be at least Schedule 40 pipe.

b.  Well casings or extensions shall extend vertically at least 2’ above the ground level.

This distance shall be increased if the well is in an area subject to flooding.

c.   All casing joints above perforations or screens shall be watertight.

SECTION III.  SEALS

For all wells which terminate in bedrock, a permanent casing shall extend from 2’ above

ground into the bedrock and a minimum of 10 feet below bedrock surfaces.

SECTION IV.  SURFACE CONSTRUCTION

a.	Openings into the top of the well which are not designed to provide access shall be sealed.  All access openings into the well shall be protected against entrance of surface water.

b.	All wells shall be vented unless they are pumped under negative pressure.

SECTION V.  WATER QUALITY SAMPLING

Sampling shall be done immediately following development and disinfection of the well.  Approval of the Board of Health must be obtained before the well water is used.  Water quality analyses shall be performed as follows:

a.	The sample shall be analyzed by a Massachusetts-certified laboratory.

b.	Bacterial quality:  The samples shall be collected after all traces of disinfectant chemicals have been removed.  The results of the bacteriological analysis shall be zero  (0) coliform per 100 ml.

c.	Chemical quality:  The sample shall be analyzed for and shall not exceed the following standards:

1.  Nitrate						10 mg. per liter

2.  Nitrite						1 mg. per liter

3.  Arsenic						0.01 mg. per liter

4.  Sodium						20 mg. per liter

Exceeding the Sodium standard does not constitute a violation but serves as a

notice to the user.

5. Gross Alpha, if 15pCi/L is triggered, then specify for uranium levels.

d.	Physical Quality

1.	Color – 15 color units.

2.	Turbidity – one (1) N.T.U.

3.	PH – 6.5  to 8.5

SECTION VI.  YIELD TEST

a.	Test pumping shall be conducted for four hours at a rate at least equal to the expected normal pumping rate.

b.	The pumping test shall be performed by a qualified pump or well drilling contractor.

c.	The results of the yield test shall be submitted to the Paxton Board of Health.

d.	The minimum well yield shall conform to the following table.

Depths of water in Well					Gals./Min. for 4 hours

0-150 feet							 5 gals/min

150-200 feet						 4 gals/min

200-250 feet						 3 gals/min

250-300 feet						  2 gals/min

300 & over						  1 gal/min

SECTION VII.  GENERAL ENFORCEMENT

The provisions of Title I of the Massachusetts Environmental Code (310 CMR

11.00) shall govern the enforcement of these regulations.

SECTION VII.  SEVERABILITY

If any section or sentence, clause, or phrase thereof shall be held invalid for any

reason, the remainder of that section and all other sections shall continue in full force and effect.